## Blad1 (2)
600
Current - Normal Case
suction | suction |  | discharge | discharge | discharge | Discharge |  | R | DEV | R^(X) | DEV* | (1000/R)^X | DEV** | Shaft | System |  | Inlet pressure (bat. limit) |  |  | 298675 | Pa (g)
vol.flow | vol.flow | mass flow | pressure | density | vol.flow | temp. | Δp | ρin·qvin2/Δp | SLV3-R | 0.33333 |  | 0.5 |  | power | curve |  | Dp inlet accessories |  |  | 3849.3514 | Pa
am3/s | am3/h | kg/s | mbar+ | kg/Am3 | am3/h |  | Pa | m4 | [5 empty] | kW |  |  | Dp inlet control valve |  |  | 8195.5 | Pa
0.86089 | 3099.2207 | 3.5685 | 471916.6091 | 4.794 | 2679.7089 | 120.5366 | 185286.6091 | 214.8797 | 385.1203 | 5.9896 | 2.4447 | 2.1573 | 0.86626 | 317.7753 | 26765.6013 |  | Inlet blower | Pressure |  | 286630 | Pa(g)
1.1989 | 4316.1069 | 4.9696 | 470967.736 | 4.9303 | 3628.7376 | 109.0227 | 184337.736 | 418.8944 | 181.1056 | 7.4823 | 0.95203 | 1.5451 | 0.25407 | 383.2648 | 50475.9648 |  |  | Pressure |  | 387955 | Pa(a)
1.5369 | 5532.9931 | 6.3708 | 467007.4166 | 4.9942 | 4592.2608 | 101.5185 | 180377.4166 | 703.5136 | -103.5136 | 8.8939 | -0.45954 | 1.1922 | -0.098754 | 442.0052 | 81888.6193 |  |  | Temperature |  | 35 | C
1.875 | 6749.8793 | 7.7719 | 460246.1798 | 5.0106 | 5583.8878 | 95.848 | 173616.1798 | 1087.7679 | -487.7679 | 10.2844 | -1.8501 | 0.95881 | -0.33219 | 494.017 | 121470.1501 |  |  | Density |  | 4.1451 | kg/Am³
2.213 | 7966.7655 | 9.1731 | 450700.2838 | 4.9891 | 6619.0527 | 91.1435 | 164070.2838 | 1603.4985 | -1003.4985 | 11.7046 | -3.2703 | 0.78971 | -0.50129 | 539.1324 | 169947.4876 |  |  | Flow |  | 7793.7913 | Am³/h
2.551 | 9183.6517 | 10.5742 | 438294.9251 | 4.9333 | 7716.3582 | 86.9837 | 151664.9251 | 2305.0485 | -1705.0485 | 13.2097 | -4.7754 | 0.65866 | -0.63234 | 577.0576 | 228383.4649 |  | Outlet blower | Pressure |  | 449100 | Pa
2.889 | 10400.5379 | 11.9753 | 422890.0932 | 4.8443 | 8899.4023 | 83.1317 | 136260.0932 | 3290.617 | -2690.617 | 14.8739 | -6.4396 | 0.55127 | -0.73973 | 607.3757 | 298300.1789 |  |  | Density |  | 4.9945 | kg/Am³
3.2271 | 11617.4241 | 13.3765 | 404282.1966 | 4.7213 | 10199.5783 | 79.4357 | 117652.1966 | 4755.0388 | -4155.0388 | 16.8158 | -8.3815 | 0.45859 | -0.83241 | 629.5256 | 381881.7763 |  |  | Flow |  | 6468.261 | Am³/h
3.5651 | 12834.3103 | 14.7776 | 382193.1782 | 4.5623 | 11660.6794 | 75.784 | 95563.1782 | 7144.7807 | -6544.7807 | 19.2603 | -10.826 | 0.37412 | -0.91688 | 642.7623 | 482317.7722 |  | Dp outlet accessories |  |  | 420.0347 | Pa
3.5651 | 12834.3103 | 14.7776 | 382193.1782 | 4.5623 | 11660.6794 | 75.784 | 95563.1782 | 7144.7807 | -6544.7807 | 19.2603 | -10.826 | 0.37412 | -0.91688 | 642.7623 | 482317.7722 |  | Pressure upst. Valve |  |  | 448675.2586 | Pa (g)
[8 empty] | 33.2501 |  | 3.2156 | [6 empty] | Dp outlet control valve |  |  | 0.25859 | Pa
[17 empty] | Outlet pressure (bat. limit) |  |  | 448675 | Pa (g)
Note: SLV's in software defined in terms of R, not as qvin
[17 empty] | dashed lines in graph |  |  | margin 1 | 15%
[17 empty] | -100 | 200000 |  | margin 2 | 15%
[17 empty] | 4294 | 4294 | <-- | SLV1
[17 empty] | 4938.1 | 4938.1 | <-- | SLV2=SLV1*(1+margin1)
[17 empty] | 5678.815 | 5678.815 | <-- | SLV3=SLV2*(1+margin1)
[17 empty] | 7794 | 7794 | <-- | design point
SLV1
[17 empty] | 183400 | Pa
[17 empty] | 4294 | Am3/h
[17 empty] | 4.145 | kg/m3
[17 empty] | 416.7247 |  |  |  | 3
[17 empty] | SLV3 | 551.1185 |  |  | 4
5
[17 empty] | 1.2039 | 1.4154 | qvin/qvout |  | 3486784401
[17 empty] | 1.4154 | 1.8724 |  |  | 3486784401
1.2173
0.82149
valve K*
[17 empty] | 21.9664 |  | 155600 | Pa
Fan curve |  | Δp= | -0.001003 | Q^2 + | 6.8043 | Q+ | 173639 | [9 empty] | 23.1225 |  | 4.22 | kg/Am3
Fan curve |  | Δp/ρ= | -0.00024197 | Q^2 + | 1.6415 | Q+ | 41890.241 | [9 empty] | 25.0514 |  | 4810.4009 | Am3/h
System curve |  | Δp/ρ= | 1/(Ksystem+Kbypass)^2 |  |  | Q^2
Operating point |  | Ksystem= | Qout/(Δp/ρout)^0,5 |  | = | 35.8632
Bypass |  | Kbypass= | 23.8 | stroke
Valve stroke |  | %stroke= | 0.0625 | mA + | -0.25
[14 empty] | output ASC |  | valve
Step | Ksystem | Kbypass |  | a | Q | Δp/ρ | Δp | [6 empty] | 4-20mA |  | stroke |  | Kbypass_new
1 | 35.8632 | 0 | --> | -0.0010195 | 7265.5895 | 41043.4795 | 170129.0935 | --> | [5 empty] | 4 | --> | 0 | --> | 0
2 | 20 | 0 | --> | -0.002742 | 4219.4117 | 44508.5886 | 184492.2976 | --> | [5 empty] | 6 | --> | 0.125 | --> | 2.975
3 | 20 | 2.975 | --> | -0.0021364 | 4828.8338 | 44174.6872 | 183108.2449 | --> | [5 empty] | 20 | --> | 1 | --> | 23.8
3 | 0 | 23.8 | --> | -0.0020074 | 4995.2925 | 44052.2335 | 182600.6628 | --> | [5 empty] | 20 | --> | 1 | --> | 23.8
NB | The flow resistance of the bypass has been assumed to equal the flow resistance of the blow off valve.

## Blad1
Current - Normal Case
suction | suction |  | discharge | discharge | discharge | Discharge |  |  | Shaft | System |  | Inlet pressure (bat. limit) |  |  | 298675 | Pa (g)
vol.flow | vol.flow | mass flow | pressure | density | vol.flow | temp. | Δp | ρin·qvin2/Δp | power | curve |  | Dp inlet accessories |  |  | 3849.3514 | Pa
am3/s | am3/h | kg/s | mbar+ | kg/Am3 | am3/h |  | Pa | m4 | kW | Pa |  | Dp inlet control valve |  |  | 8195.5 | Pa
0.86089 | 3099.2207 | 3.5685 | 471916.6091 | 4.794 | 2679.7089 | 120.5366 | 185286.6091 | 214.8797 | 317.7753 | 25690.9784 |  | Inlet blower | Pressure |  | 286630 | Pa | 387955
1.1989 | 4316.1069 | 4.9696 | 470967.736 | 4.9303 | 3628.7376 | 109.0227 | 184337.736 | 418.8944 | 383.2648 | 49826.4588 |  |  | Density |  | 4.1451 | kg/Am³
1.5369 | 5532.9931 | 6.3708 | 467007.4166 | 4.9942 | 4592.2608 | 101.5185 | 180377.4166 | 703.5136 | 442.0052 | 81883.4053 |  |  | Flow |  | 7793.7913 | Am³/h
1.875 | 6749.8793 | 7.7719 | 460246.1798 | 5.0106 | 5583.8878 | 95.848 | 173616.1798 | 1087.7679 | 494.017 | 121861.818 |  | Outlet blower | Pressure |  | 449100 | Pa
2.213 | 7966.7655 | 9.1731 | 450700.2838 | 4.9891 | 6619.0527 | 91.1435 | 164070.2838 | 1603.4985 | 539.1324 | 169761.6967 |  |  | Density |  | 4.9945 | kg/Am³
2.551 | 9183.6517 | 10.5742 | 438294.9251 | 4.9333 | 7716.3582 | 86.9837 | 151664.9251 | 2305.0485 | 577.0576 | 225583.0415 |  |  | Flow |  | 6468.261 | Am³/h
2.889 | 10400.5379 | 11.9753 | 422890.0932 | 4.8443 | 8899.4023 | 83.1317 | 136260.0932 | 3290.617 | 607.3757 | 289325.8525 |  | Dp outlet accessories |  |  | 420.0347 | Pa
3.2271 | 11617.4241 | 13.3765 | 404282.1966 | 4.7213 | 10199.5783 | 79.4357 | 117652.1966 | 4755.0388 | 629.5256 | 360990.1295 |  | Pressure upst. Valve |  |  | 448675.2586 | Pa (g)
3.5651 | 12834.3103 | 14.7776 | 382193.1782 | 4.5623 | 11660.6794 | 75.784 | 95563.1782 | 7144.7807 | 642.7623 | 440575.8727 |  | Dp outlet control valve |  |  | 0.25859 | Pa
3.5651 | 12834.3103 | 14.7776 | 382193.1782 | 4.5623 | 11660.6794 | 75.784 | 95563.1782 | 7144.7807 | 642.7623 | 440575.8727 |  | Outlet pressure (bat. limit) |  |  | 448675 | Pa (g)
[14 empty] | Tin | 35 | C
[12 empty] | dashed lines in graph |  |  | margin 1 | 15%
[12 empty] | -100 | 200000 |  | margin 2 | 15%
[12 empty] | 4294 | 4294 | <-- | SLV1
[12 empty] | 4938.1 | 4938.1 | <-- | SLV2=SLV1*(1+margin1)
[12 empty] | 5678.815 | 5678.815 | <-- | SLV3=SLV2*(1+margin1)
[12 empty] | 7794 | 7794 | <-- | design point
SLV1
[12 empty] | 183400 | Pa
[12 empty] | 4294 | Am3/h
[12 empty] | 4.145 | kg/m3
[12 empty] | 416.7247 |  |  |  | 3
4
5
[12 empty] | 1.2039 | 1.5668 |  |  | 3486784401
[12 empty] | 1.5668 | 2.4203 |  |  | 3486784401
1.2173
0.82149
valve K*
[12 empty] | 21.9664 |  | 155600 | Pa
Fan curve |  | Δp= | -0.001003 | Q^2 + | 6.8043 | Q+ | 173639 |  |  |  |  | 23.1225 |  | 4.22 | kg/Am3
Fan curve |  | Δp/ρ= | -0.00024197 | Q^2 + | 1.6415 | Q+ | 41890.241 |  |  |  |  | 25.0514 |  | 4810.4009 | Am3/h
System curve |  | Δp/ρ= | 1/(Ksystem+Kbypass)^2 |  |  | Q^2
Operating point |  | Ksystem= | Q/(Δp/ρ)^0,5 |  | = | 39.3667
Bypass |  | Kbypass= | 23.8 | stroke
Valve stroke |  | %stroke= | 0.0625 | mA + | -0.25
[9 empty] | output ASC |  | valve
Step | Ksystem | Kbypass |  | a | Q | Δp/ρ | Δp |  | 4-20mA |  | stroke |  | Kbypass_new
1 | 39.3667 | 0 | --> | -0.00088724 | 7858.3089 | 39847.3474 | 165171.0132 | --> | 4 | --> | 0 | --> | 0
2 | 20 | 0 | --> | -0.002742 | 4219.4117 | 44508.5886 | 184492.2976 | --> | 6 | --> | 0.125 | --> | 2.975
3 | 20 | 2.975 | --> | -0.0021364 | 4828.8338 | 44174.6872 | 183108.2449 | --> | 20 | --> | 1 | --> | 23.8
3 | 0 | 23.8 | --> | -0.0020074 | 4995.2925 | 44052.2335 | 182600.6628 | --> | 20 | --> | 1 | --> | 23.8
NB | The flow resistance of the bypass has been assumed to equal the flow resistance of the blow off valve.

## Blad2
Kv waarden Blow Off Valve (Masoneilan 35002 series)
Diameter | [Inch] | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12
| [mm] | 25 | 40 | 50 | 80 | 100 | 150 | 200 | 250 | 300
Orifice | [mm] | 14.7 | 23 | 29.4 | 47.6 | 61.4 | 92.2 | 123 | 154 | 189
Cv bij opening | 10% | 0.6 | 1.4 | 2.1 | 5.7 | 9.7 | 21.2 | 31.3 | 47.8 | 64.4
| 20% | 1.3 | 3.2 | 4.8 | 12.1 | 20.7 | 44.9 | 63.6 | 97.3 | 131
| 30% | 2.2 | 5.1 | 7.7 | 19.6 | 33.4 | 72.7 | 114 | 175 | 235
| 40% | 3.1 | 7.4 | 1.2 | 27.6 | 47 | 102 | 178 | 273 | 367
| 50% | 4.2 | 10 | 15.1 | 37.5 | 63.8 | 139 | 246 | 376 | 506
| 60% | 5.3 | 12.7 | 19.1 | 47.9 | 81.6 | 177 | 313 | 478 | 644
| 70% | 6.4 | 15 | 22.7 | 58.4 | 99.4 | 216 | 374 | 572 | 769
| 80% | 7.2 | 17.1 | 25.8 | 68 | 116 | 252 | 425 | 650 | 875
| 90% | 7.9 | 18.6 | 28.2 | 75.9 | 129 | 281 | 468 | 716 | 694
| 100% | 8.4 | 19.8 | 30 | 81 | 138 | 300 | 510 | 780 | 1050